## READ ME FIRST
VoltServer™ Digital Electricity™ Gen2E Compatible Cable Table
SUMMARY
This document provides guidance for Digital Electricity compatible cables for VoltServer's Gen3 Fault Managed Power (FMPS) Class 4 deployments, based on the compatibility, ratings, and specifications of different cable types. The document explains how to use the VoltServer CL4 Cable Table, which lists the manufacturers, part numbers, pair counts, and minimum wire gauges for various deployment environments. For Gen2E LPS, refer to the VoltServer Gen2E LPS cable table.
PURPOSE
◊ The purpose of this document is to provide Designers, Integrators, Project Managers, and Installers with an easy reference for cabling solutions for VoltServer Remote Powering deployments. ◊ Cable ratings, color coding, and construction are extracted from the cable manufacturers datasheets. ◊ All cables used with the VoltServer Gen3 FMPS must be certified to UL 1400-2. ◊ If a required cable type is not in this Cable Table (i.e. ratings, pair count, etc.) please contact VoltServer Support, espeically in discussions with cable manufacturers and suppliers to ensure suitability of proposed product(s).
HOW TO USE THE VOLTSERVER CABLE TABLE | CABLE RATING LEGEND
◊ Refer to deployment Venue Package to determine the minimum gauge and pair count required to each location. Contact your poject manager or system designer to obtain the Venue Package. ◊ Determine the rating required for each cable run. i.e. Plenum, Riser, Outdoor, mixed, etc. ◊ Refer to the appropriate page in this document for deployment rating. ◊ Lookup the required pairs for the remote location(s). ◊ Lookup the minimum conductor gauge (AWG) for the remote as stated in the Venue Package. ◊ Look up the Part Numbers for the desired manufacturer. | Cable Rating Legend CL4 = General Purpose Cable, Class 4, 450 V, Certified to UL 1400-2, May be used outdoors and/or direct burial. CL3 = General Purpose Cable, Class 3, 300 V CMP, CL4P, CL3P = All in-wall plenum & riser applications. CMR, CL4R, CL3R = All in-wall and riser applications, not permitted in plenum spaces. CM, CMG = In-wall rated; permitted in 1-2 family residential riser applications, or in riser with raceway/fireproof shaft, not permitted in plenum spaces. CL4Z = Covers cables designated that are intended for outdoor use only and are not to be attached to, or used within a building structure. Permitted to also be designated “CL4P”, “CL4R” or “CL4”.
BEST PRACTICES
◊ The deployment environment must be considered to ensure a suitably rated cable type is ordered. i.e. DO NOT use Plenum or Riser rated cable outdoors. ◊ VoltServer recommends that additional conductor pairs be included in the initial builds to provide for future growth (Dark Copper). ◊ If required, to help standardize on a single cable type for a deployment where the Design Document or Venue Package indicates a number of different minimum gauges, the next larger gauge can be used. i.e. Increase 16AWG runs to 14 AWG runs to standardize on 14AWG. ◊ DO NOT reduce gauge from required minimum gauge i.e. from 16AWG to 18AWG - this will invalidate the VoltServer Design, may NOT be covered by warranty, and could violate local or national electrical code. ◊ If a cable run transitions from one tating area to another, i.e. from Plenum to Outdoor, a splice will be necessary adjacent to the transition. ◊ Refer to the DE Best Practices Guide for required methods and practices for intermediate splices.
NOTES
◊ Lowercase letters within a part number denotes that these parameters do not affect DE compatibility (i.e. fiber count).
Customer Support: support@voltserver.com | CONFIDENTIAL & PROPRIETARY | 2025-03-01
888-622-8658, Option 1 | www.VoltServer.com | Rev 1

## Indoor Plenum & Riser
Gen2E Approved Indoor Plenum & Riser Cables Required for Plenum Deployments. Plenum cable may be used in risers
Manufacturer |  | Belden | Remee | Remee | GCG | Corning | Corning | Tessco | CommScope | Windy City
Cable Family |  | FMPS Cables | PowerPipe™ | PowerPipe™ | Electrowire™ | ActiFi® | ActiFi® |  | Constellation®
Pair Construction |  | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair | Linear Lay | Linear Lay | Linear Lay | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4P, CMP, LS-PVC | CL4P, CMP | CMP | CL3P, FT6 | CL4P | CL3P | CL3P, CMP, LS-PVC | CL4P, CMP | CMP, LS-PVC
AWG | Pairs | Part Number
18 | 1 |  | DE1P18RRM1WE |  |  |  | xxxyzb8-21V01M20
| 2 | DEIP182U | DE2P18RRM1WE | 2P18RRM1WE | EWP182PRC |  |  | 589156
| 3 |  | DE3P18RRM1WE | 3P18RRM1WE | EWP183PRC | 006ZT8-61N01N20 | xxxZT8-41V01M20
| 4 | DEIP184U | DE4P18RRM1WE | 4P18RRM1WE | EWP184PRC |  | xxxZT8-61V01M20
| 6 |  | DE6P18RRM1WE | 6P18RRM1WE |  |  | xxxZT8-61V01M20
| 8 | DEIP188U | DE8P18RRM1WE | 8P18RRM1WE | EWP188PRC | 006ZT8-M1N01M20
16 | 1 |  | DE1P16RRM1WE |  |  |  | xxxyZT8-21Y01M20
| 2 | DEIP162U | DE2P16RRM1WE | 2P16RRM1WE | EWP162PRC
| 3 |  | DE3P16RRM1WE | 3P16RRM1WE | EWP163PRC |  | xxxZT8-41Y01M20
| 4 | DEIP164U | DE4P16RRM1WE | 4P16RRM1WE | EWP164PRC |  | xxxZT8-61Y01M20 | 564155 | P-016-HY-8G-F30YL/4X16AWG/CTX | 164PPDIGIELEC
| 6 |  | DE6P16RRM1WE | 6P16RRM1WE | EWP166PRC |  | xxxZT8-61Y01M20
| 8 | DEIP168U | DE8P16RRM1WE | 8P16RRM1WE | EWP168PRC | 012ZT8-M1N01N20 |  | 545844
Features |  | Features
Hybrid Fiber Available |  | Optional | Yes | No | No | Yes | Yes |  | Yes | No
Country of Origin |  | Mexico | USA | USA | USA | USA | USA |  | Mexico | USA
Shielded/Armored |  | No | No | No | No | No | No | No | No | No
Jacket Color |  | Green | Natural/Green | Natural/Green | White | Yellow | Yellow | Black, White | Yellow | Black
Wire Color Codes |  | Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | Black/Red | Black/Red | Telcordia | Telcordia | Black/Red | Red/White | White/Blue
Pair #2 |  | Black/White | Black/White | Black/White | Black/White |  |  | White/Green | Black/White | White/Orange
Pair #3 |  | Black/Green | Black/Green | Black/Green | Black/Green |  |  | Brown/Blue | Blue/White | White/Green
Pair #4 |  | Black/Blue | Black/Blue | Black/Blue | Black/Blue |  |  | Orange/Yellow | Brown/White | White/Brown
Pair #5 |  | Black/Yellow | Black/Yellow | Black/Yellow | Black/Yellow |  |  | Purrple/Gray |  | White/Gray
Pair #6 |  | Black/Brown | Black/Brown | Black/Brown | Black/Brown |  |  | Pink/Tan |  | Red/Blue
Pair #7 |  | Black/Orange | Black/Orange | Black/Orange | Black/Orange |  |  | White/Black |  | Red/Orange
Pair #8 |  | Red/White | Red/White | Red/White | Red/White |  |  | White/Green |  | Red/Green

## Indoor Riser
Gen2E Approved Indoor Riser Cables CL4R, CL3R, CMG, and CMR rated cable NOT permitted in plenum
Manufacturer |  | Belden | Belden | Corning | Marmon
Cable Family |  | FMPS Cables | FMPS Cables | ActiFi® | COM-Link®
Pair Construction |  | Twisted Pair | Twisted Pair | Linear Lay | Twisted Pair
Compliance Standards |  | CL4Z, CMG, Wet Locations, Sun Resistant | CL4Z, CMG, Wet Locations, Sun Resistant | CL3R | CL4Z, CL3, CMG, Wet Locations, Sun Resistant
AWG | Pairs | Part Number
18 | 1 |  |  | xxxZTF-21V01M20 | C4C-RFT40U01-18-1SR/W-0
| 2 | DEDN182U | DEDN182F | xxxZTF-41V01M20 | C4C-RFT40U01-18-2SR/W-0
| 3 |  |  | xxxZTF-61V01M20 | C4C-RFT40U01-18-3SR/W-0
| 4 | DEDN184U | DEDN184F |  | C4C-RFT40U01-18-4SR/W-0
| 6 |  |  | xxxZTF-M1V01M20 | C4C-RFT40U01-18-6SR/W-0
| 8 | DEDN188U | DEDN188F |  | C4C-RFT40U01-18-8SR/W-0
16 | 1 |  |  | xxxZTF-21Y01M20 | C4C-RFT40U01-16-1SR/W-0
| 2 | DEDN162U | DEDN162F | xxxZTF-41Y01M20 | C4C-RFT40U01-16-2SR/W-0
| 3 |  |  | xxxZTF-61Y01M20 | C4C-RFT40U01-16-3SR/W-0
| 4 | DEDN164U | DEDN164F |  | C4C-RFT40U01-16-4SR/W-0
| 6 |  |  | xxxZTF-M1Y01M20 | C4C-RFT40U01-16-6SR/W-0
| 8 | DEDN168U | DEDN168F |  | C4C-RFT40U01-16-8SR/W-0
Features |  | Features
Hybrid Fiber Available |  | Optional | Yes | Yes | No
Country of Origin |  | Mexico | USA | USA | USA
Shielded/Armored |  | No | No | No | No
Jacket Color |  | Green | Natural/Green | Yellow | Natural/Green
Wire Color Codes |  | Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | Telcordia | Black/Red
Pair #2 |  | Black/White | Black/White |  | Black/White
Pair #3 |  | Black/Green | Black/Green |  | Black/Green
Pair #4 |  | Black/Blue | Black/Blue |  | Black/Blue
Pair #5 |  | Black/Yellow | Black/Yellow |  | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown |  | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange |  | Black/Orange
Pair #8 |  | Black/White | Black/White |  | Black/White

## GP Indoor-Outdoor
Gen2E Approved General Purpose Indoor/Outdoor Cables Not for continuous wet, outdoor ducts, or direct burial
Manufacturer |  | Belden | Belden | Marmon | GCG | TiniFiber | TiniFiber
Cable Family |  | FMPS Cables | FMPS Cables | COM-Link® | Electrowire™ | Micro Armor Fiber™ | Micro Armor Fiber™
Pair Construction |  | Twisted Pair | Twisted Pair | Twisted Pair |  | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4Z, CMG, Wet Locations, Sun Resistant | CL4Z, CMG, Wet Locations, Sun Resistant | CL4Z, CMG, Wet Locations, Sun Resistant | CL3, FT4, PLTC, Wet Locations Sun Resistant | CL4 | CL4
AWG | Pairs | Part Number
18 | 1 |  |  | C4C-RFT40U01-18-1SR/W-0
| 2 | DEDN182U | DEDN182F | C4C-RFT40U01-18-2SR/W-0 |  | PTFxx-OS2-18/2-PLO | PTFxx-OS2-18/2-PL
| 3 |  |  | C4C-RFT40U01-18-3SR/W-0 | EWTX182PR
| 4 | DEDN184U | DEDN184F | C4C-RFT40U01-18-4SR/W-0 | EWTX162PR | PTFxx-OS2-18/4-PLO | PTFxx-OS2-18/4-PL
| 6 |  |  | C4C-RFT40U01-18-6SR/W-0 |  | PTFxx-OS2-18/6-PLO | PTFxx-OS2-18/6-PL
| 8 | DEDN188U | DEDN188F | C4C-RFT40U01-18-8SR/W-0 | EWTX163PR
16 | 1 |  |  | C4C-RFT40U01-16-1SR/W-0 | EWTX184PR
| 2 | DEDN162U | DEDN162F | C4C-RFT40U01-16-2SR/W-0 | EWTX164PR | PTFxx-OS2-16/2-PLO | PTFxx-OS2-16/2-PL
| 3 |  |  | C4C-RFT40U01-16-3SR/W-0
| 4 | DEDN164U | DEDN164F | C4C-RFT40U01-16-4SR/W-0 | EWTX166PR | PTFxx-OS2-16/4-PLO | PTFxx-OS2-16/4-PL
| 6 |  |  | C4C-RFT40U01-16-6SR/W-0 | EWTX188PR | PTFxx-OS2-16/6-PLO | PTFxx-OS2-16/6-PL
| 8 | DEDN168U | DEDN168F | C4C-RFT40U01-16-8SR/W-0 | EWTX168PR
Features |  | Features
Hybrid Fiber Available |  | Optional | Yes | No | No | Yes | Yes
Country of Origin |  | Mexico | USA | USA | USA
Shielded/Armored |  | No | No | No | No | Yes | Yes
Jacket Color |  | Green | Natural/Green | Natural/Green | White | Black | Black
Wire Color Codes |  | Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | Black/Red | Black/Red
Pair #2 |  | Black/White | Black/White | Black/White | Black/White
Pair #3 |  | Black/Green | Black/Green | Black/Green | Black/Green
Pair #4 |  | Black/Blue | Black/Blue | Black/Blue | Black/Blue
Pair #5 |  | Black/Yellow | Black/Yellow | Black/Yellow | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown | Black/Brown | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange | Black/Orange | Black/Orange
Pair #8 |  | Black/White | Black/White | Black/White | Red/White

## Wet Locations
Gen2E Approved Wet Location Cables Rated for wet locations, outdoor ducts, not direct burial.
Manufacturer |  | Belden | Belden | Marmon | GCG
Cable Family |  | FMPS Cables | FMPS Cables | COM-Link® | Electrowire™
Pair Construction |  | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4Z, CMG, Wet Locations, Sun Resistant | CL4Z, CMG, Wet Locations, Sun Resistant | CL4Z, CMG, Wet Locations, Sun Resistant | CL3, FT4, PLTC, Wet Locations Sun Resistant
AWG | Pairs | Part Number
18 | 1 |  |  | C4C-RFT40U01-18-1SR/W-0
| 2 | DEDN182U | DEDN182F | C4C-RFT40U01-18-2SR/W-0
| 3 |  |  | C4C-RFT40U01-18-3SR/W-0 | EWTX182PR
| 4 | DEDN184U | DEDN184F | C4C-RFT40U01-18-4SR/W-0 | EWTX162PR
| 6 |  |  | C4C-RFT40U01-18-6SR/W-0
| 8 | DEDN188U | DEDN188F | C4C-RFT40U01-18-8SR/W-0 | EWTX163PR
16 | 1 |  |  | C4C-RFT40U01-16-1SR/W-0 | EWTX184PR
| 2 | DEDN162U | DEDN162F | C4C-RFT40U01-16-2SR/W-0 | EWTX164PR
| 3 |  |  | C4C-RFT40U01-16-3SR/W-0
| 4 | DEDN164U | DEDN164F | C4C-RFT40U01-16-4SR/W-0 | EWTX166PR
| 6 |  |  | C4C-RFT40U01-16-6SR/W-0 | EWTX188PR
| 8 | DEDN168U | DEDN168F | C4C-RFT40U01-16-8SR/W-0 | EWTX168PR
Features |  | Features
Hybrid Fiber Available |  | Optional | Optional | No | No
Country of Origin |  | Mexico | Mexico | USA | USA
Shielded/Armored |  | No | Shielded | No | No
Jacket Color |  | Black | Black | Black | Black
Wire Color Codes |  | Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | Black/Red | Black/Red
Pair #2 |  | Black/White | Black/White | Black/White | Black/White
Pair #3 |  | Black/Green | Black/Green | Black/Green | Black/Green
Pair #4 |  | Black/Blue | Black/Blue | Black/Blue | Black/Blue
Pair #5 |  | Black/Yellow | Black/Yellow | Black/Yellow | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown | Black/Brown | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange | Black/Orange | Black/Orange
Pair #8 |  | Black/White | Black/White | Red/White | Red/White

## Direct Burial
Gen2E Approved Direct Burial Cables
Manufacturer |  | Remee | Remee | Windy City | EUPEN | Proterial | Boldyn
Cable Family |  | PowerPipe™ | PowerPipe™ | Outdoor Line Power
Pair Construction |  | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4Z, Direct Burial, Sun Resistant | CL4Z, Direct Burial, Sun Resistant | CMR, Direct Burial | CL4, Wet Locations Direct Burial, Sun Resistant | CL4Z, Direct Burial, Sun Resistant | CL4, Wet Locations Direct Burial, Sun Resistant
AWG | Pairs | Part Number
18 | 1 | DE1P18ISOSPB2B | DE1P18OSPB2B
| 2 | DE2P18ISOSPB2B | DE2P18OSPB2B
| 3 | DE3P18ISOSPB2B | DE3P18OSPB2B
| 4 | DE4P18ISOSPB2B | DE4P18OSPB2B
| 6 | DE6P18ISOSPB2B | DE6P18OSPB2B
| 8 | DE8P18ISOSPB2B | DE8P18OSPB2B
16 | 1 | DE1P16ISOSPB2B | DE1P16OSPB2B
| 2 | DE2P16ISOSPB2B | DE2P16OSPB2B
| 3 | DE3P16ISOSPB2B | DE3P16OSPB2B
| 4 | DE4P16ISOSPB2B | DE4P16OSPB2B | 164PDBDIGIELEC
| 6 | DE6P16SOSPB2B | DE6P16OSPB2B
| 8 | DE8P16ISOSPB2B | DE8P16OSPB2B |  | HP16X16-CL4-B | WPN01613783 | BN16X16-CL4-B
Features |  | Features
Hybrid Fiber Available |  | Yes | Yes | No | No | No | No
Country of Origin |  | USA | USA | USA | USA |  | USA
Shielded/Armored |  | Shielded | No | No | No | No | No
Jacket Color |  | Black | Black | Black | Black | Black | Black
Wire Color Codes |  | Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | White/Blue | Black/Red | Black/Red | Black/Red
Pair #2 |  | Black/White | Black/White | White/Orange | Black/White | Black/White | Black/White
Pair #3 |  | Black/Green | Black/Green | White/Green | Black/Green | Black/Green | Black/Green
Pair #4 |  | Black/Blue | Black/Blue | White/Brown | Black/Blue | Black/Blue | Black/Blue
Pair #5 |  | Black/Yellow | Black/Yellow | White/Gray | Black/Yellow | Black/Yellow | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown | Red/Blue | Black/Brown | Black/Brown | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange | Red/Orange | Black/Orange | Black/Orange | Black/Orange
Pair #8 |  | Red/White | Red/White | Red/Green | Red/White | Red/White | Red/White

## MFR Info
Cable Manufacturer Website | How to buy/contact | Product info
Southwire | Southwire - Where-to-Buy | Southwire CL4SS™ Class 4 Non-Shielded Gen. Purpose Outdoor
Southwire CL4SS™ Class 4 Shielded Outdoor / General Purpose
Belden | Belden - Find-A-Distributor | Belden FMPS Cables
Remee | Remee - Request for Information | Remee - Activate Powered Cable Solutions
CommScope | CommScope - How to Buy | CommScope - Constellation Plenum Hybrid Class 4 Cable
Windy City | Windy City - Contact Us | WCW - Digital Electricity Cables
Corning | Corning Authorized Distributors | Corning - Actifi
Genuine Cable Group (GCG) | Shop GCG | GCG - Line Power Cable
Marmon | Marmon - Contact US | Marmon - COM-link cables
Tinifiber | Tinifiber - Request a Quote
Proterial | Proterial - Sales Offices | Proterial - Cable Systems
Tessco | Tessco - Support