## READ ME FIRST
SUMMARY
This document provides guidance for Digital Electricity compatible cables for VoltServer's Gen3 Fault Managed Power (FMPS) Class 4 deployments, based on the compatibility, ratings, and specifications of different cable types. The document explains how to use the VoltServer CL4 Cable Table, which lists the manufacturers, part numbers, pair counts, and minimum wire gauges for various deployment environments. For Gen2E LPS, refer to the VoltServer Gen2E LPS cable table.
PURPOSE
◊ The purpose of this document is to provide Designers, Integrators, Project Managers, and Installers with an easy reference for cabling solutions for VoltServer Remote Powering deployments. ◊ Cable ratings, color coding, and construction are extracted from the cable manufacturers datasheets. ◊ All cables used with the VoltServer Gen3 FMPS must be certified to UL 1400-2. ◊ If a required cable type is not in this Cable Table (i.e. ratings, pair count, etc.) please contact VoltServer Support, espeically in discussions with cable manufacturers and suppliers to ensure suitability of proposed product(s).
HOW TO USE THE VOLTSERVER CABLE TABLE | CABLE RATING LEGEND
◊ Refer to deployment Venue Package to determine the minimum gauge and pair count required to each location. Contact your poject manager or system designer to obtain the Venue Package. ◊ Determine the rating required for each cable run. i.e. Plenum, Riser, Outdoor, mixed, etc. ◊ Refer to the appropriate page in this document for deployment rating. ◊ Lookup the required pairs for the remote location(s). ◊ Lookup the minimum conductor gauge (AWG) for the remote as stated in the Venue Package. ◊ Look up the Part Numbers for the desired manufacturer. | Cable Rating Legend CL4 = General Purpose Cable, Class 4, 450 V, Certified to UL 1400-2, May be used outdoors and/or direct burial. CL3 = General Purpose Cable, Class 3, 300 V CMP, CL4P, CL3P = All in-wall plenum & riser applications. CMR, CL4R, CL3R = All in-wall and riser applications, not permitted in plenum spaces. CM, CMG = In-wall rated; permitted in 1-2 family residential riser applications, or in riser with raceway/fireproof shaft, not permitted in plenum spaces. CL4Z = Covers cables designated that are intended for outdoor use only and are not to be attached to, or used within a building structure. Permitted to also be designated “CL4P”, “CL4R” or “CL4”.
BEST PRACTICES
◊ The deployment environment must be considered to ensure a suitably rated cable type is ordered. i.e. DO NOT use Plenum or Riser rated cable outdoors. ◊ VoltServer recommends that additional conductor pairs be included in the initial builds to provide for future growth (Dark Copper). ◊ If required, to help standardize on a single cable type for a deployment where the Design Document or Venue Package indicates a number of different minimum gauges, the next larger gauge can be used. i.e. Increase 16AWG runs to 14 AWG runs to standardize on 14AWG. ◊ DO NOT reduce gauge from required minimum gauge i.e. from 16AWG to 18AWG - this will invalidate the VoltServer Design, may NOT be covered by warranty, and could violate local or national electrical code. ◊ If a cable run transitions from one tating area to another, i.e. from Plenum to Outdoor, a splice will be necessary adjacent to the transition. ◊ Refer to the DE Best Practices Guide for required methods and practices for intermediate splices.
NOTES
◊ Lowercase letters within a part number denotes that these parameters do not affect DE compatibility (i.e. jacket color, fiber count, etc.)

## Indoor Plenum & Riser
Class 4 Approved Indoor Plenum & Riser Required for Plenum Deployments. Plenum cable may be used in risers.
Manufacturer |  | Southwire | Belden | Belden | Remee | Corning | CommScope
Cable Family |  | CL4SS® | FMPS Cables | FMPS Cables | PowerPipe™ | ActiFi® | Constellation®
Pair Construction |  | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair | Linear Lay | Twisted Pair
Compliance Standards |  | CL4Z, CMP, LS-PVC | CL4P, CMP, LS-PVC | CL4P, CMP, LS-PVC | CL4P, CMP | CL4P | CL4P, CMP
AWG | Pairs |  | Part Number
18 | 1 | CL4Z181N060x |  |  | DE1P18RRM1WE
| 2 | CL4Z182N060x | DEIP182U | DEIP182F | DE2P18RRM1WE
| 3 | CL4Z183N060x |  |  | DE3P18RRM1WE
| 4 | CL4Z184N060x | DEIP184U | DEIP184F | DE4P18RRM1WE
| 6 | CL4Z186N060x |  |  | DE6P18RRM1WE
| 8 | CL4Z188N060x | DEIP188U | DEIP188F | DE8P18RRM1WE
16 | 1 | CL4Z161N060x |  |  | DE1P16RRM1WE
| 2 | CL4Z162N060x | DEIP162U | DEIP162F | DE2P16RRM1WE
| 3 | CL4Z163N060x |  |  | DE3P16RRM1WE
| 4 | CL4Z164N060x | DEIP164U | DEIP164F | DE4P16RRM1WE |  | P-016-HY-8G-F30YL/4X16AWG/CTX
| 6 | CL4Z166N060x |  |  | DE6P16RRM1WE | xxxZT8-M1N01N20
| 8 | CL4Z168N060x | DEIP168U | DEIP168F | DE8P16RRM1WE
14 | 1 | CL4Z141N060x |  |  | DE1P14RRM1WE
| 2 | CL4Z142N060x | DEIP142U | DEIP142F | DE2P14RRM1WE
| 3 | CL4Z143N060x |  |  | DE3P14RRM1WE
| 4 | CL4Z144N060x | DEIP144U | DEIP144F | DE4P14RRM1WE
| 6 | CL4Z146N060x |  |  | DE6P14RRM1WE
| 8 | CL4Z148N060x | DEIP148U | DEIP148F | DE8P14RRM1WE
12 | 1
2
3
4
6
8
Features
Hybrid Fiber Available |  | No | Yes | Yes | Yes | Yes | Yes
Country of Origin |  | USA | Mexico | Mexico | USA | USA | USA
Shielded/Armored |  | Yes | No | Yes | No | No | No
Jacket Color |  | Green or Black | Green | Green | Natural w/ Green Stripe | Yellow | Yellow
Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | Black/Red | Black/Red | Telcordia | Red/White
Pair #2 |  | Black/White | Black/White | Black/White | Black/White |  | Black/White
Pair #3 |  | Black/Green | Black/Green | Black/Green | Black/Green |  | Blue/White
Pair #4 |  | Black/Blue | Black/Blue | Black/Blue | Black/Blue |  | Brown/White
Pair #5 |  | Black/Yellow | Black/Yellow | Black/Yellow | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown | Black/Brown | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange | Black/Orange | Black/Orange
Pair #8 |  | Black/White | Red/White | Black/White | Red/White

## Indoor Riser
Class 4 Indoor Riser Cables CMG, CL4R, CL3R, CMR not permitted in plenum
Manufacturer |  | Corning | Belden | Southwire
Cable Family |  | ActiFi® | FMPS Cables | CL4SS™
Pair Construction |  | Linear Lay | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4R | CL4, CMG, Sun Resistant | CL4Z, CMG
AWG | Pairs | Part Number
18 | 1
| 2 |  | DEDN182U | CL4Z182S060x
3
| 4 |  | DEDN184U | CL4Z184S060x
6
| 8 |  | DEDN188U | CL4Z188S060x
16 | 1
| 2 |  | DEDN162U | CL4Z162S060x
3
| 4 |  | DEDN164U | CL4Z164S060x
| 6 | xxxZTF-M1N01N20
| 8 |  | DEDN168U | CL4Z168S060x
14 | 1
| 2 |  | DEDN142U | CL4Z142S060x
3
| 4 |  | DEDN144U | CL4Z144S060x
6
| 8 |  | DEDN148U | CL4Z148S060x
12 | 1
2
3
4
6
8
Features
Hybrid Fiber Available |  | Yes | Optional | No
Country of Origin |  | USA | Mexico | USA
Shielded/Armored |  | No | No | Yes
Jacket Color |  | Yellow | Black | Yellow
Wire Color Codes
Pair #1 |  | Telcordia | Black/Red | Black/Red
Pair #2 |  |  | Black/White | Black/White
Pair #3 |  |  | Black/Green | Black/Green
Pair #4 |  |  | Black/Blue | Black/Blue
Pair #5 |  |  | Black/Yellow | Black/Yellow
Pair #6 |  |  | Black/Brown | Black/Brown
Pair #7 |  |  | Black/Orange | Black/Orange
Pair #8 |  |  | Black/White | Black/White

## Gen. Purp. In-Outdoor
Class 4 General Purpose Indoor/ Outdoor Not rated for continuous wet locations, in conduit/ducts, or direct burial.
Manufacturer |  | Belden | Southwire | Southwire
Cable Family |  | FMPS Cables | CL4SS® | CL4SS™
Pair Construction |  | Twisted Pair | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4, CMG, Sun Resistant | CL4Z, CMP, LS-PVC | CL4Z, CMG
AWG | Pairs | Part Number
18 | 1 |  | CL4Z181N060x | CL4Z181S060x
| 2 | DEDN182U | CL4Z182N060x | CL4Z182S060x
| 3 |  | CL4Z183N060x | CL4Z183S060x
| 4 | DEDN184U | CL4Z184N060x | CL4Z184S060x
| 6 |  | CL4Z186N060x | CL4Z186S060x
| 8 | DEDN188U | CL4Z188N060x | CL4Z188S060x
16 | 1 |  | CL4Z161N060x | CL4Z161S060x
| 2 | DEDN162U | CL4Z162N060x | CL4Z162S060x
| 3 |  | CL4Z163N060x | CL4Z163S060x
| 4 | DEDN164U | CL4Z164N060x | CL4Z164S060x
| 6 |  | CL4Z166N060x | CL4Z166S060x
| 8 | DEDN168U | CL4Z168N060x | CL4Z168S060x
14 | 1 |  | CL4Z141N060x | CL4Z141S060x
| 2 | DEDN142U | CL4Z142N060x | CL4Z142S060x
| 3 |  | CL4Z143N060x | CL4Z143S060x
| 4 | DEDN144U | CL4Z144N060x | CL4Z144S060x
| 6 |  | CL4Z146N060x | CL4Z146S060x
| 8 | DEDN148U | CL4Z148N060x | CL4Z148S060x
12 | 1
2
3
4
6
8
Features
Hybrid Fiber Available |  | Optional | No | No
Country of Origin |  | Mexico | USA | USA
Shielded/Armored |  | No | Yes | Yes
Jacket Color |  | Black | Green or Black | Yellow
Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | Black/Red
Pair #2 |  | Black/White | Black/White | Black/White
Pair #3 |  | Black/Green | Black/Green | Black/Green
Pair #4 |  | Black/Blue | Black/Blue | Black/Blue
Pair #5 |  | Black/Yellow | Black/Yellow | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange | Black/Orange
Pair #8 |  | Black/White | Black/White | Black/White

## Wet Locations
Class 4 Wet Location Cables Rated for wet locations, outdoor ducts, not direct burial.
Manufacturer |  | Belden | Marmon
Cable Family |  | FMPS Cables | COM-Link®
Pair Construction |  | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4Z, CMG, Wet Locations, Sun Resistant | CL4Z, FT4, Wet Location, Sun Resistant
AWG | Pairs | Part Number
18 | 1 |  | C4C-RFT40U01-18-1SR/W-0
| 2 | DEDN182F | C4C-RFT40U01-18-2SR/W-0
| 3 |  | C4C-RFT40U01-18-3SR/W-0
| 4 | DEDN184F | C4C-RFT40U01-18-4SR/W-0
| 6 |  | C4C-RFT40U01-18-6SR/W-0
| 8 | DEDN188F | C4C-RFT40U01-18-8SR/W-0
16 | 1 |  | C4C-RFT40U01-16-1SR/W-0
| 2 | DEDN162F | C4C-RFT40U01-16-2SR/W-0
| 3 |  | C4C-RFT40U01-16-3SR/W-0
| 4 | DEDN164F | C4C-RFT40U01-16-4SR/W-0
| 6 |  | C4C-RFT40U01-16-6SR/W-0
| 8 | DEDN168F | C4C-RFT40U01-16-8SR/W-0
14 | 1 |  | C4C-RFT40U01-14-1SR/W-0
| 2 | DEDN142F | C4C-RFT40U01-14-2SR/W-0
| 3 |  | C4C-RFT40U01-14-3SR/W-0
| 4 | DEDN144F | C4C-RFT40U01-14-4SR/W-0
| 6 |  | C4C-RFT40U01-14-6SR/W-0
| 8 | DEDN148F | C4C-RFT40U01-14-8SR/W-0
12 | 1
2
3
4
6
8
Features
Hybrid Fiber Available |  | Optional | No
Country of Origin |  | Mexico | USA
Shielded/Armored |  | No | Optional
Jacket Color |  | Black | Black
Wire Color Codes
Pair #1 |  | Black/Red | Black/Red
Pair #2 |  | Black/White | Black/White
Pair #3 |  | Black/Green | Black/Green
Pair #4 |  | Black/Blue | Black/Blue
Pair #5 |  | Black/Yellow | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange
Pair #8 |  | Black/White | Red/White

## Direct Burial
Class 4 Direct Burial Cables
Manufacturer |  | Remee | EUPEN | Proterial | Boldyn
Cable Family |  | PowerPipe™
Pair Construction |  | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair
Compliance Standards |  | CL4Z, Direct Burial, Sun Resistant | CL4, Direct Burial, Sun Resistant | CL4Z, Direct Burial, Sun Resistant | CL4, Direct Burial, Sun Resistant
AWG | Pairs | Part Number
18 | 1 | DE1P18OSPB2B
| 2 | DE2P18OSPB2B
| 3 | DE3P18OSPB2B
| 4 | DE4P18OSPB2B
| 6 | DE6P18OSPB2B
| 8 | DE8P18OSPB2B
16 | 1 | DE1P16OSPB2B
| 2 | DE2P16OSPB2B
| 3 | DE3P16OSPB2B
| 4 | DE4P16OSPB2B
| 6 | DE6P16OSPB2B
| 8 | DE8P16OSPB2B | HP16X16-CL4-B | WPN01613783 | BN16X16-CL4-B
14 | 1 | DE1P14OSPB2B
| 2 | DE2P14OSPB2B
| 3 | DE3P14OSPB2B
| 4 | DE4P14OSPB2B
| 6 | DE6P14OSPB2B
| 8 | DE8P14OSPB2B | - |  | -
12 | 1
2
3
4
6
8
Features
Hybrid Fiber Available |  | Yes | No | No | No
Country of Origin |  | USA | USA |  | USA
Shielded/Armored |  | No | No | No | No
Jacket Color |  | Green | Black | Black | Black
Wire Color Codes
Pair #1 |  | Black/Red | Black/Red | Black/Red | Black/Red
Pair #2 |  | Black/White | Black/White | Black/White | Black/White
Pair #3 |  | Black/Green | Black/Green | Black/Green | Black/Green
Pair #4 |  | Black/Blue | Black/Blue | Black/Blue | Black/Blue
Pair #5 |  | Black/Yellow | Black/Yellow | Black/Yellow | Black/Yellow
Pair #6 |  | Black/Brown | Black/Brown | Black/Brown | Black/Brown
Pair #7 |  | Black/Orange | Black/Orange | Black/Orange | Black/Orange
Pair #8 |  | Red/White | Red/White | Red/White | Red/White

## MFR Information
Cable Manufacturer Website | How to buy/contact | Product info
Southwire | Southwire - Where-to-Buy | Southwire CL4SS™ Class 4 Non-Shielded Gen. Purpose Outdoor
Southwire CL4SS™ Class 4 Shielded Outdoor / General Purpose
Belden | Belden - Find-A-Distributor | Belden FMPS Cables
Remee | Remee - Request for Information | Remee Activate Powered Cable Solutions
CommScope | CommScope - How to Buy | Constellation Plenum Hybrid Class 4 Cable
Corning | Corning Authorized Distributors | Actifi Composite Cables
Marmon | Marmon - Contact US | Marmon - COM-link cables
Tinifiber | Tinifiber - Request a Quote | Why TiniFiber
EUPEN | EUPEN - Contact Us
Proterial | Proterial - Sales Offices | Proterial - Cable Systems

## dropdown menus (hidden)
Cable Rating | Cable Gauge (AWG) | # of Pairs
All | All | All
Indoor Plenum | 18 | 1
Indoor Riser | 16 | 2
Indoor/Outdoor | 14 | 3
Outdoor Wet Locations &/or Direct Burial | 12 | 4
6
8

## Not Available (hidden)
NO LONGER AVAILABLE |  |  | NO LONGER AVAILABLE |  |  | NO LONGER AVAILABLE |  |  | NO LONGER AVAILABLE |  |  | NO LONGER AVAILABLE
Manufacturer | Electrowire | Belden | Tessco | Windy City | Electrowire | Belden | Tessco | Windy City | Electrowire | Corning | Okonite | Belden | Windy City | Belden | Electrowire | Corning | Windy City
Family |  | Digital Electricity™ |  |  |  | Digital Electricity™ | [5 empty] | Digital Electricity™ |  | Digital Electricity™
Pair Construction | Linear Lay | Twisted Pair | Linear Lay | Twisted Pair | Linear Lay | Twisted Pair | Linear Lay | Twisted Pair | Twisted Pair | Linear Lay | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair | Twisted Pair | Linear Lay | Twisted Pair
Markings | CL3P, FPLP FT6 | CL4P, CMP, LS-PVC, TC | CMP, CL3P, FPLP, LS-PVC | CMP, LS-PVC | CL3P, FPLP FT6 | CL4P, CMP, LS-PVC, TC | CMP, CL3P, FPLP, LS-PVC | CMP, LS-PVC | Wet Locations, CL3, FT4, PLTC, Sun Resistant | CL3R | Wet Locations, CL2, CL3, PLTC, ITC, FPL, FT4, Sun Resistant | Wet Locations, CL4, CMG, Sun Resistant, | Direct Burial, CMR | CL4, CL3, CMG, Sun Resistant | Enhanced Waterblocking, CL3, CMG, Sun Resistant | CL3, PLTC, FT4, LSZH (H), Sun Resistant | CMR, Direct Burial
Conductor Guage | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number | Part Number
1 Pair, 2 Conductor
18AWG | [8 empty] | - | - | - | - | - | - | - | - | -
16AWG | [8 empty] | - | - | - | - | - | - | - | - | -
14AWG | [8 empty] | - | - | - |  | - |  | - | - | -
2 Pair, 4 Conductor
18AWG | EWP184C |  |  | - | EWP184C |  |  | - | DEDL182U | EWTX184C | 260-10-3602 |  | - |  | DEDL182U | EWTX184C | 2P18PVCWBTM1B
16AWG | EWP164C |  | 589155 | - | EWP164C |  | 589155 | - | DEDL162U | EWTX164C | 260-10-3502 |  | - |  | DEDL162U | EWTX164C | 2P16PVCWBTM1B
14AWG | EWP144C |  | - | - | EWP144C |  | - | - | DEDL142U | EWTX144C | - |  | - |  | DEDL142U | EWTX144C | 2P14PVCWBTM1B
3 Pair, 6 Conductor
18AWG | EWP186C | DEIP183U | - | - | EWP186C | DEIP183U | - |  | - | - | 260-10-3603 | - | - | - | - | - | -
16AWG | EWP166C | DEIP163U | - | - | EWP166C | DEIP163U | - | - | DEDL163U | EWTX166C | 260-10-3503 | DEDN163U | - | DEDN163U | DEDL163U | EWTX166C | -
14AWG | EWP146C | DEIP143U | - | - | EWP146C | DEIP143U | - | - | DEDL143U | EWTX146C | - | DEDN143U | - | DEDN143U | DEDL143U | EWTX146C | -
4 Pair, 8 Conductor
18AWG | EWP188C |  | 564156 | 184PPDIGIELEC | EWP188C |  | 564156 | 184PPDIGIELEC | DEDL184U | EWTX188C | 260-10-3604 |  | 184PDBDIGIELEC |  | DEDL184U | EWTX188C | 4P18PVCWBTM1B
16AWG | EWP168C |  |  |  | EWP168C |  |  |  | DEDL164U | EWTX168C | 260-10-3504 |  |  |  | DEDL164U | EWTX168C | 4P16PVCWBTM1B
14AWG | EWP148C |  | - | - | EWP148C |  | - | - | DEDL144U | EWTX148C | - |  |  |  | DEDL144U | EWTX148C | 4P14PVCWBTM1B
6 Pair, 12 Conductor
18AWG | - | - | - | - | - | - | - | - | - | - | 260-10-3606 | - | - | - | - | - | 8P18PVCWBTM1B
16AWG | EWP1612C | DEIP166U | - | - | EWP1612C | DEIP166U | - | - | DEDL166U | EWTX1612C | 260-10-3506 | DEDN166U | - | DEDN166U | DEDL166U | EWTX1612C | 8P16PVCWBTM1B
14AWG | EWP1412C | DEIP146U | - | - | EWP1412C | DEIP146U | - | - | DEDL146U | EWTX1412C | - | DEDN146U | - | DEDN146U | DEDL146U | EWTX1412C | 8P14PVCWBTM1B
8 Pair, 16 Conductor
18AWG | EWP1816C |  | 545843 | 188PPDIGIELEC | EWP1816C |  | 545843 | 188PPDIGIELEC | DEDL188U | EWTX1816C | 260-10-3608 |  | 188PDBDIGIELEC |  | DEDL188U | EWTX1816C | -
16AWG | EWP1616C |  |  | 168PPDIGIELEC | EWP1616C |  |  | 168PPDIGIELEC | DEDL168U | EWTX1616C | 260-10-3508 |  | 168PDBDIGIELEC |  | DEDL168U | EWTX1616C | -
14AWG | EWP1416C |  | - | - | EWP1416C |  | - | - | DEDL148U | EWTX1416C | - |  | - |  | DEDL148U | EWTX1416C | -
Misc. Information
Features |  | Flamarrest® Apple Green Jacket with ripcord |  |  |  | Flamarrest® Apple Green Jacket with ripcord |  | White Jacket w/Green stripe
Pair #1 Color Codes | White/Blue | with Ripcord | Black/Red | Black/Red | White/Blue | Black/Red | Black/Red | Black/Red | White/Blue |  | Pairs are identified with black print on the white conductor of each white/black pair | Black/Red | Black/Red | Black/Red | White/Blue |  | Black/Red
Pair #2 Color Codes | White/Orange | Black/White | White/Green | Black/White | White/Orange | Black/White | White/Green | Black/White | White/Orange |  |  | Black/White | Black/White | Black/White | White/Orange |  | Black/White
Pair #3 Color Codes | White/Green | Black/Green | Brown/Blue | Black/Green | White/Green | Black/Green | Brown/Blue | Black/Green | White/Green |  |  | Black/Green | Black/Green | Black/Green | White/Green |  | Black/Green
Pair #4 Color Codes | White/Brown | Black/Blue | Orange/Yellow | Black/Blue | White/Brown | Black/Blue | Orange/Yellow | Black/Blue | White/Brown |  |  | Black/Blue | Black/Blue | Black/Blue | White/Brown |  | Black/Blue
Pair #5 Color Codes | White/Gray | Black/Yellow | Purrple/Gray |  | White/Gray | Black/Yellow | Purrple/Gray |  | White/Gray |  |  | Black/Yellow |  | Black/Yellow | White/Gray |  | -
Pair #6 Color Codes | Red/Blue | Black/Brown | Pink/Tan |  | Red/Blue | Black/Brown | Pink/Tan |  | Red/Blue |  |  | Black/Brown |  | Black/Brown | Red/Blue |  | -
Pair #7 Color Codes | Red/Orange | Black/Orange | White/Black |  | Red/Orange | Black/Orange | White/Black |  | Red/Orange |  |  | Black/Orange |  | Black/Orange | Red/Orange |  | -
Pair #8 Color Codes | Red/Green | Red/White | White/Green |  | Red/Green | Red/White | White/Green |  | Red/Green |  |  | Red/White |  | Red/White | Red/Green |  | -
Pair #9 Color Codes | Red/Brown | - | White/Orange |  | Red/Brown | - | White/Orange |  | Red/Brown |  |  | - |  | - | Red/Brown |  | -
Pair #10 Color Codes | Red/Gray | - |  |  | Red/Gray | - |  |  | Red/Gray |  |  | - |  | - | Red/Gray |  | -
Pair #11 Color Codes | Black/Blue | - |  |  | Black/Blue | - |  |  | Black/Blue |  |  | - |  | - | Black/Blue |  | -
Pair #12 Color Codes | Black/Orange | - |  |  | Black/Orange | - |  |  | Black/Orange |  |  | - |  | - | Black/Orange |  | -
Pair #13 Color Codes | Black/Green | - |  |  | Black/Green | - |  |  | Black/Green |  |  | - |  | - | Black/Green |  | -
Pair #14 Color Codes | Black/Brown | - |  |  | Black/Brown | - |  |  | Black/Brown |  |  | - |  | - | Black/Brown |  | -
Pair #15 Color Codes | Black/Gray | - |  |  | Black/Gray | - |  |  | Black/Gray |  |  | - |  | - | Black/Gray |  | -
Pair #16 Color Codes |  | - |  |  |  | - | [5 empty] | - |  | - | - |  | -