## READ ME
User Guide - Class 2/LPS Approved Cables
Follow the guide below to select the cable you need. Only approved cables may be used with Class 2/LPS, or the system may not be covered by warranty.
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Step | Decision | Required input | Design Notes
1 | Determine deployment environment for each cable run segment | Plenum, Riser, Wet locations, or Direct Burial. | A single route may require more than one cable construction.
2 | Determine cable rating | Select the listing required for each segment. | A higher indoor fire rating does not make a cable outdoor or wet-rated.
3 | Determine minimum gauge | Use the minimum conductor gauge stated in the Venue Package. | Never reduce conductor size below the specified minimum.
4 | Determine required pair count | Use the Venue Package pair requirement for each remote location. | Consider spare pairs for future growth where practical.
5 | Select approved cable | Filter the approved cable list by environment, rating, gauge, and pair count. | Do not start with manufacturer preference.
6 | Select manufacturer and part number | Choose among compliant options based on availability and project constraints. | Verify the current manufacturer datasheet before procurement.

## SELECTION GUIDE
VoltServer Class 2-LPS Cable Selection Guide
Filter by environment, rating, minimum AWG, pair count, manufacturer, or feature
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Environment | Full Cable Ratings | AWG | # Pairs | Manufacturer | Cable family | Part number | Pair construction | Hybrid Fiber Available | Shielded/ Armored | Jacket Color | Source URL
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 1 | Remee | PowerPipe | DE1P18ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 1 | Remee | PowerPipe | DE1P16OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 1 | Remee | PowerPipe | DE1P16ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 2 | Remee | PowerPipe | DE2P18OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 2 | Remee | PowerPipe | DE2P18ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 2 | Remee | PowerPipe | DE2P16OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 2 | Remee | PowerPipe | DE2P16ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 3 | Remee | PowerPipe | DE3P18OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 3 | Remee | PowerPipe | DE3P18ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 3 | Remee | PowerPipe | DE3P16OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 3 | Remee | PowerPipe | DE3P16ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 4 | Remee | PowerPipe | DE4P18OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 4 | Remee | PowerPipe | DE4P18ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 4 | Remee | PowerPipe | DE4P16OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 4 | Remee | PowerPipe | DE4P16ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CMR / Direct Burial | 16 | 4 | Windy City Wire | Outdoor Line Power | 164PDBDIGIELEC | Twisted Pair | No | No
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 6 | Remee | PowerPipe | DE6P18OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 6 | Remee | PowerPipe | DE6P18ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 6 | Remee | PowerPipe | DE6P16OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 6 | Remee | PowerPipe | DE6P16ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 8 | Remee | PowerPipe | DE8P18OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 8 | Remee | PowerPipe | DE8P18ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 8 | Remee | PowerPipe | DE8P16OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 16 | 8 | Remee | PowerPipe | DE8P16ISOSPxxx | Twisted Pair | Yes | Shielded | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4 / Wet / Direct Burial / Sun Resistant | 16 | 8 | EUPEN | Outdoor Cable | HP16X16-CL4-B | Twisted Pair | No | No
Direct Burial | CL4 / Wet / Direct Burial / Sun Resistant | 16 | 8 | Proterial | Cable Systems | WPN01613783 | Twisted Pair | No | No
Direct Burial | CL4Z / Direct Burial / Sun Resistant | 18 | 1 | Remee | PowerPipe | DE1P18OSPxxx | Twisted Pair | Yes | No | Black | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CMP | 18 | 1 | Remee | PowerPipe | DE1P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CMP | 16 | 1 | Remee | PowerPipe | DE1P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CL3P | 18 | 1 | Marmon IEI | COM-Link | C4C-P00U02-18-01 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 1 | Marmon IEI | COM-Link | C4C-P00U02-16-01 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CMP / LS-PVC | 18 | 2 | Belden | FMPS Cables | DEIP182U | Twisted Pair | No | Optional | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP182U
Plenum | CL4P / CMP / LS-PVC | 18 | 2 | Belden | FMPS Cables | DEIP182F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP182F
Plenum | CL4P / CMP / LS-PVC | 16 | 2 | Belden | FMPS Cables | DEIP162U | Twisted Pair | No | Optional | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP162U
Plenum | CL4P / CMP / LS-PVC | 16 | 2 | Belden | FMPS Cables | DEIP162F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP162F
Plenum | CL4P / CMP | 18 | 2 | Remee | PowerPipe | DE2P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CMP | 16 | 2 | Remee | PowerPipe | DE2P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CL3P | 18 | 2 | Marmon IEI | COM-Link | C4C-P00U02-18-02 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 2 | Marmon IEI | COM-Link | C4C-P00U02-16-02 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL3P / FPLP / FT6 | 18 | 2 | GCG | Electrowire | EWP182PRC | Twisted Pair | No | No
Plenum | CL3P / FPLP / FT6 | 16 | 2 | GCG | Electrowire | EWP162PRC | Twisted Pair | No | No
Plenum | CL3P / CMP / FPLP / LS-PVC | 18 | 2 | Tessco | Constellation | 589156 | Twisted Pair | No | No
Plenum | CL4P / CMP | 18 | 3 | Remee | PowerPipe | DE3P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CMP | 16 | 3 | Remee | PowerPipe | DE3P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CL3P | 18 | 3 | Marmon IEI | COM-Link | C4C-P00U02-18-03 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 3 | Marmon IEI | COM-Link | C4C-P00U02-16-03 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CMP / LS-PVC | 18 | 4 | Belden | FMPS Cables | DEIP184U | Twisted Pair | No | Optional | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP184U
Plenum | CL4P / CMP / LS-PVC | 18 | 4 | Belden | FMPS Cables | DEIP184F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP184F
Plenum | CL4P / CMP / LS-PVC | 16 | 4 | Belden | FMPS Cables | DEIP164U | Twisted Pair | No | Optional | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP164U
Plenum | CL4P / CMP / LS-PVC | 16 | 4 | Belden | FMPS Cables | DEIP164F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP164F
Plenum | CL4P / CMP | 18 | 4 | Remee | PowerPipe | DE4P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CMP | 16 | 4 | Remee | PowerPipe | DE4P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CL3P | 18 | 4 | Marmon IEI | COM-Link | C4C-P00U02-18-04 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 4 | Marmon IEI | COM-Link | C4C-P00U02-16-04 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL3P / FPLP / FT6 | 18 | 4 | GCG | Electrowire | EWP184PRC | Twisted Pair | No | No
Plenum | CL3P / FPLP / FT6 | 16 | 4 | GCG | Electrowire | EWP164PRC | Twisted Pair | No | No
Plenum | CMP / LS-PVC | 18 | 4 | Windy City Wire | Digital Electricity | 184PPDIGIELEC | Twisted Pair | No | No
Plenum | CMP / LS-PVC | 16 | 4 | Windy City Wire | Digital Electricity | 164PPDIGIELEC | Twisted Pair | No | No
Plenum | CL3P / CMP / FPLP / LS-PVC | 16 | 4 | Tessco | Constellation | 564155 | Twisted Pair | No | No
Plenum | CL3P / CMP / FPLP / LS-PVC | 16 | 4 | Southwire | CL4SS | P50017-25 | Twisted Pair | No | No
Plenum | CL4P / CMP | 18 | 6 | Remee | PowerPipe | DE6P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CMP | 16 | 6 | Remee | PowerPipe | DE6P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CL3P | 18 | 6 | Marmon IEI | COM-Link | C4C-P00U02-18-06 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 6 | Marmon IEI | COM-Link | C4C-P00U02-16-06 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CMP / LS-PVC | 18 | 8 | Belden | FMPS Cables | DEIP188U | Twisted Pair | No | Optional | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP188U
Plenum | CL4P / CMP / LS-PVC | 18 | 8 | Belden | FMPS Cables | DEIP188F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP188F
Plenum | CL4P / CMP / LS-PVC | 16 | 8 | Belden | FMPS Cables | DEIP168U | Twisted Pair | No | Optional | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP168U
Plenum | CL4P / CMP / LS-PVC | 16 | 8 | Belden | FMPS Cables | DEIP168F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP168F
Plenum | CL4P / CMP | 18 | 8 | Remee | PowerPipe | DE8P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CMP | 16 | 8 | Remee | PowerPipe | DE8P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Plenum | CL4P / CL3P | 18 | 8 | Marmon IEI | COM-Link | C4C-P00U02-18-08 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 8 | Marmon IEI | COM-Link | C4C-P00U02-16-08 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL3P / FPLP / FT6 | 18 | 8 | GCG | Electrowire | EWP188PRC | Twisted Pair | No | No
Plenum | CL3P / FPLP / FT6 | 16 | 8 | GCG | Electrowire | EWP168PRC | Twisted Pair | No | No
Plenum | CMP / LS-PVC | 18 | 8 | Windy City Wire | Digital Electricity | 188PPDIGIELEC | Twisted Pair | No | No
Plenum | CL3P / CMP / FPLP / LS-PVC | 16 | 8 | Tessco | Constellation | 545844 | Twisted Pair | No | No
Plenum | CL3P / CMP / FPLP / LS-PVC | 16 | 8 | Southwire | CL4SS | P50061-25 | Twisted Pair | No | No
Plenum | CL4P / CL3P | 18 | 12 | Marmon IEI | COM-Link | C4C-P00U02-18-12 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 12 | Marmon IEI | COM-Link | C4C-P00U02-16-12 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 18 | 16 | Marmon IEI | COM-Link | C4C-P00U02-18-16 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Plenum | CL4P / CL3P | 16 | 16 | Marmon IEI | COM-Link | C4C-P00U02-16-16 | Twisted Pair | Yes | No | White/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4Z / CMG / Wet / Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182U
Riser | CL4Z / CMG / Wet / Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182F
Riser | CL4Z / CMG / Wet / Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162U
Riser | CL4Z / CMG / Wet / Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162F
Riser | CL4Z / CMG / Wet / Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184U
Riser | CL4Z / CMG / Wet / Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184F
Riser | CL4Z / CMG / Wet / Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164U
Riser | CL4Z / CMG / Wet / Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164F
Riser | CL4Z / CMG / Wet / Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188U
Riser | CL4Z / CMG / Wet / Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188F
Riser | CL4Z / CMG / Wet / Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168U
Riser | CL4Z / CMG / Wet / Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168F
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 1 | Marmon IEI | COM-Link | C4C-R00U01-18-01SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 1 | Marmon IEI | COM-Link | C4C-R00U01-16-01SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 2 | Marmon IEI | COM-Link | C4C-R00U01-18-02SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 2 | Marmon IEI | COM-Link | C4C-R00U01-16-02SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 3 | Marmon IEI | COM-Link | C4C-R00U01-18-03SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 3 | Marmon IEI | COM-Link | C4C-R00U01-16-03SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 4 | Marmon IEI | COM-Link | C4C-R00U01-18-04SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 4 | Marmon IEI | COM-Link | C4C-R00U01-16-04SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 6 | Marmon IEI | COM-Link | C4C-R00U01-18-06SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 6 | Marmon IEI | COM-Link | C4C-R00U01-16-06SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 8 | Marmon IEI | COM-Link | C4C-R00U01-18-08SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 8 | Marmon IEI | COM-Link | C4C-R00U01-16-08SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 12 | Marmon IEI | COM-Link | C4C-R00U01-18-12SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 12 | Marmon IEI | COM-Link | C4C-R00U01-16-12SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 18 | 16 | Marmon IEI | COM-Link | C4C-R00U01-18-16SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R / CL3R / Wet / Sun Resistant | 16 | 16 | Marmon IEI | COM-Link | C4C-R00U01-16-16SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 1 | Marmon IEI | COM-Link | C4H-R00U01-18-01SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 1 | Marmon IEI | COM-Link | C4H-R00U01-16-01SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 2 | Marmon IEI | COM-Link | C4H-R00U01-18-02SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 2 | Marmon IEI | COM-Link | C4H-R00U01-16-02SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 3 | Marmon IEI | COM-Link | C4H-R00U01-18-03SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 3 | Marmon IEI | COM-Link | C4H-R00U01-16-03SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 4 | Marmon IEI | COM-Link | C4H-R00U01-18-04SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 4 | Marmon IEI | COM-Link | C4H-R00U01-16-04SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 6 | Marmon IEI | COM-Link | C4H-R00U01-18-06SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 6 | Marmon IEI | COM-Link | C4H-R00U01-16-06SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 8 | Marmon IEI | COM-Link | C4H-R00U01-18-08SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 8 | Marmon IEI | COM-Link | C4H-R00U01-16-08SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 12 | Marmon IEI | COM-Link | C4H-R00U01-18-12SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 12 | Marmon IEI | COM-Link | C4H-R00U01-16-12SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 16 | Marmon IEI | COM-Link | C4H-R00U01-18-16SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Riser | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 16 | Marmon IEI | COM-Link | C4H-R00U01-16-16SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4Z / CMG / Wet / Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182U
Wet | CL4Z / CMG / Wet / Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182F
Wet | CL4Z / CMG / Wet / Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162U
Wet | CL4Z / CMG / Wet / Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162F
Wet | CL4Z / CMG / Wet / Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184U
Wet | CL4Z / CMG / Wet / Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184F
Wet | CL4Z / CMG / Wet / Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164U
Wet | CL4Z / CMG / Wet / Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164F
Wet | CL4Z / CMG / Wet / Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188U
Wet | CL4Z / CMG / Wet / Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188F
Wet | CL4Z / CMG / Wet / Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168U | Twisted Pair | No | Optional | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168U
Wet | CL4Z / CMG / Wet / Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168F
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 1 | Marmon IEI | COM-Link | C4C-R00U01-18-01SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 1 | Marmon IEI | COM-Link | C4C-R00U01-16-01SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 2 | Marmon IEI | COM-Link | C4C-R00U01-18-02SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 2 | Marmon IEI | COM-Link | C4C-R00U01-16-02SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 3 | Marmon IEI | COM-Link | C4C-R00U01-18-03SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 3 | Marmon IEI | COM-Link | C4C-R00U01-16-03SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 4 | Marmon IEI | COM-Link | C4C-R00U01-18-04SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 4 | Marmon IEI | COM-Link | C4C-R00U01-16-04SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 6 | Marmon IEI | COM-Link | C4C-R00U01-18-06SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 6 | Marmon IEI | COM-Link | C4C-R00U01-16-06SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 8 | Marmon IEI | COM-Link | C4C-R00U01-18-08SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 8 | Marmon IEI | COM-Link | C4C-R00U01-16-08SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 12 | Marmon IEI | COM-Link | C4C-R00U01-18-12SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 12 | Marmon IEI | COM-Link | C4C-R00U01-16-12SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 18 | 16 | Marmon IEI | COM-Link | C4C-R00U01-18-16SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R / CL3R / Wet / Sun Resistant | 16 | 16 | Marmon IEI | COM-Link | C4C-R00U01-16-16SW | Twisted Pair | No | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 1 | Marmon IEI | COM-Link | C4H-R00U01-18-01SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 1 | Marmon IEI | COM-Link | C4H-R00U01-16-01SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 2 | Marmon IEI | COM-Link | C4H-R00U01-18-02SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 2 | Marmon IEI | COM-Link | C4H-R00U01-16-02SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 3 | Marmon IEI | COM-Link | C4H-R00U01-18-03SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 3 | Marmon IEI | COM-Link | C4H-R00U01-16-03SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 4 | Marmon IEI | COM-Link | C4H-R00U01-18-04SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 4 | Marmon IEI | COM-Link | C4H-R00U01-16-04SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 6 | Marmon IEI | COM-Link | C4H-R00U01-18-06SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 6 | Marmon IEI | COM-Link | C4H-R00U01-16-06SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 8 | Marmon IEI | COM-Link | C4H-R00U01-18-08SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 8 | Marmon IEI | COM-Link | C4H-R00U01-16-08SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 12 | Marmon IEI | COM-Link | C4H-R00U01-18-12SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 12 | Marmon IEI | COM-Link | C4H-R00U01-16-12SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 18 | 16 | Marmon IEI | COM-Link | C4H-R00U01-18-16SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/
Wet | CL4R-OF / CL3R-OF / Wet / Sun Resistant | 16 | 16 | Marmon IEI | COM-Link | C4H-R00U01-16-16SW | Twisted Pair | Yes | No | Black/Custom | https://marmoniei.com/market/telecom/class-4/

## Environment Guide
Environment Guide
Determine the installation environment before selecting cable
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Environment | Common location | Required rating family | Selection rule | Do not assume
Plenum | Air-return ceilings and environmental air spaces | CMP, CL4P, CL3P | May also be used in risers | Do not use outdoors or in wet locations unless specifically rated.
Riser | Vertical shafts and between-floor pathways | CMR, CL4R, CL3R, CMG | Use only where plenum rating is not required | Not permitted in plenum spaces. Not wet-rated unless stated.
Indoor/Outdoor | Building exits and non-continuously-wet outdoor routing | CL4Z, CMG or specifically listed indoor/outdoor rating | Confirm building attachment and local code requirements | Not for continuous wet locations or direct burial unless stated.
Wet Locations | Outdoor conduit, ducts, and continuously wet pathways | WET plus applicable building rating | Verify sun resistance where exposed | Not direct burial unless specifically listed.
Direct Burial | Underground installation without added raceway protection | DB / DIR BUR plus applicable rating | Confirm shielding, sunlight resistance, and transition method | Transition to building-rated cable before entering spaces where required.

## Ratings Guide
Cable Rating Guide
Use project specifications and local code requirements to confirm the required listing.
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Marking | Meaning | Typical application | Engineering note
CL4 | General purpose Class 4 cable, 450 V | Outdoor and/or direct burial only when specifically listed | Certification to UL 1400-2 for Class 4 deployments.
CL3 | General purpose Class 3 cable, 300 V | General-purpose pathways subject to listing and code | 300 V rating required (do NOT use 600V)
CL4P / CMP / CL3P | Plenum | Plenum and riser | Preferred for environmental air spaces.
CL4R / CMR / CL3R | Riser | Riser and qualifying in-wall pathways | Not permitted in plenum spaces.
CM / CMG | General-purpose in-wall | Limited building applications | Not permitted in plenum spaces.
CL4Z | Outdoor-only designation | Outdoor use; building attachment limitations may apply | May appear with CL4P, CL4R, or CL4 markings.
WET | Continuous wet location | Conduit or ducts | Does not automatically mean direct burial.
DB / DIR BUR | Direct burial | Below grade without added protection | Confirm transition and building-entry requirements.

## Color Codes
Manufacturer Wire Color Codes
Use the information below for conductor maps.
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Pair # | Belden | Southwire | CommScope | MarmonIEI | Remee | Corning | EUPEN | Proterial
1 | Black/Red | Black/Red | Red/White | Black/Red | Black/Red | Telcordia | Black/Red | Black/Red
2 | Black/White | Black/White | Black/White | Black/White | Black/White |  | Black/White | Black/White
3 | Black/Green | Black/Green | Blue/White | Black/Green | Black/Green |  | Black/Green | Black/Green
4 | Black/Blue | Black/Blue | Brown/White | Black/Blue | Black/Blue |  | Black/Blue | Black/Blue
5 | Black/Yellow | Black/Yellow |  | Black/Yellow | Black/Yellow |  | Black/Yellow | Black/Yellow
6 | Black/Brown | Black/Brown |  | Black/Brown | Black/Brown |  | Black/Brown | Black/Brown
7 | Black/Orange | Black/Orange |  | Black/Orange | Black/Orange |  | Black/Orange | Black/Orange
8 | Red/White | Black/White |  | Red/White | Red/White |  | Red/White | Red/White
9 |  |  |  | Red/Green
10 |  |  |  | Red/Blue
11 |  |  |  | Red/Yellow
12 |  |  |  | Red/Brown
13 |  |  |  | Red/Orange
14 |  |  |  | White/Green
15 |  |  |  | White/Blue
16 |  |  |  | White/Yellow

## MFR Directory
Manufacturer & Procurement Directory
Confirm availability, specifications, and ordering details with the manufacturer or distributor before ordering.
Manufacturer | Cable family | Coverage in source guide | Product information
Belden | FMPS Cables | Plenum; Riser; Wet | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable
Remee | PowerPipe | Plenum; Riser; Direct Burial | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Marmon IEI | COM-Link | Plenum; Riser; Wet | https://marmoniei.com/market/telecom/class-4/
Corning | ActiFi | Plenum; Riser | https://www.corning.com/in-building-networks/worldwide/en/home/applications/local-area-networks/next-generation-lan/actifi-composite-cable.html
Southwire | CL4SS | Riser; Wet | https://www.southwire.com/
Windy City Wire | SmartWire / Digital Electricity | Plenum; Direct Burial | https://www.windycitywire.com/products/das/digital-electricity
GCG | Electrowire | Plenum; Wet; Wet | https://shop.gogcg.com/comms/cable/power-cable/line-power-cable
Tessco | Constellation | Plenum | https://www.tessco.com/
Wirewerks | Digital Electricity | Plenum; Riser | https://wirewerks.com/en/newsroom/powered-fiber-solutions-for-smarter-network-densification/
EUPEN | Outdoor cable | Direct Burial | https://eupen.us/
Proterial | Cable Systems | Direct Burial | https://us.proterial.com/materials-products/cable-systems/index.php
With deep technical expertise spanning NEC Class 4 compliance, intelligent power transmission, and real-time fault mitigation architectures, Luke is a recognized authority in designing and deploying safe, high-voltage Fault-Managed Power Systems.