## READ ME
User Guide - Class 4 FMPS Cables
Follow the guide below to select the appropriate Class 4 FMPS cable. Any UL 1400-2 rated cable may be used.
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Step | Decision | Required input | Design Notes
1 | Determine deployment environment for each cable-run segment | Plenum, Riser, Indoor/Outdoor Wet, or Direct Burial. | A single route may require more than one cable construction.
2 | Determine cable rating | Select the Class 4 listing required for each segment. | A higher indoor fire rating does not make a cable outdoor or wet-rated.
3 | Determine minimum gauge | Use the minimum conductor gauge stated in the Venue Package: 18, 16, 14, or 12 AWG. | Never reduce conductor size below the specified minimum.
4 | Determine required pair count | Use the Venue Package pair requirement for each remote location. | Consider spare pairs for future growth where practical.
5 | Select approved cable | Filter the approved cable list by environment, rating, gauge, and pair count. | Do not start with manufacturer preference.
6 | Select manufacturer and part number | Choose among compliant options based on availability and project constraints. | Verify the current manufacturer datasheet before procurement.
With deep technical expertise spanning NEC Class 4 compliance, intelligent power transmission, and real-time fault mitigation architectures, Luke is a recognized authority in designing and deploying safe, high-voltage Fault-Managed Power Systems.

## CL4 CABLE TABLE
VoltServer Gen3 Class 4 FMPS Approved Cable Selection Guide
Filter by environment, full cable ratings, minimum AWG, pair count, manufacturer, or feature
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Environment | Full Cable Ratings | AWG | # Pairs | Manufacturer | Cable family | Part number | Pair construction | Hybrid Fiber Available | Shielded/ Armored | Jacket Color | Source URL
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 1 | Remee | PowerPipe™ | DE1P12OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 1 | Remee | PowerPipe™ | DE1P12ISOSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 1 | Remee | PowerPipe™ | DE1P14OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 1 | Remee | PowerPipe™ | DE1P14OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 1 | Remee | PowerPipe™ | DE1P16OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 1 | Remee | PowerPipe™ | DE1P16OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 1 | Remee | PowerPipe™ | DE1P18OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 1 | Remee | PowerPipe™ | DE1P18OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 2 | Remee | PowerPipe™ | DE2P12OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 2 | Remee | PowerPipe™ | DE2P12ISOSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 2 | Remee | PowerPipe™ | DE2P14OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 2 | Remee | PowerPipe™ | DE2P14OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 2 | Remee | PowerPipe™ | DE2P16OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 2 | Remee | PowerPipe™ | DE2P16OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 2 | Remee | PowerPipe™ | DE2P18OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 2 | Remee | PowerPipe™ | DE2P18OSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/wp-content/uploads/2024/11/PowerPipe%E2%84%A2-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 3 | Remee | PowerPipe™ | DE3P12OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 3 | Remee | PowerPipe™ | DE3P12ISOSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 3 | Remee | PowerPipe™ | DE3P14OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 3 | Remee | PowerPipe™ | DE3P14OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 3 | Remee | PowerPipe™ | DE3P16OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 3 | Remee | PowerPipe™ | DE3P16OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 3 | Remee | PowerPipe™ | DE3P18OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 3 | Remee | PowerPipe™ | DE3P18OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 4 | Remee | PowerPipe™ | DE4P12OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 4 | Remee | PowerPipe™ | DE4P12ISOSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 4 | Remee | PowerPipe™ | DE4P14OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 4 | Remee | PowerPipe™ | DE4P14OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 4 | Remee | PowerPipe™ | DE4P16OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 4 | Remee | PowerPipe™ | DE4P16OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 4 | Remee | PowerPipe™ | DE4P18OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 4 | Remee | PowerPipe™ | DE4P18OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 6 | Remee | PowerPipe™ | DE6P12OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 6 | Remee | PowerPipe™ | DE6P12ISOSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 6 | Remee | PowerPipe™ | DE6P14OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 6 | Remee | PowerPipe™ | DE6P14OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 6 | Remee | PowerPipe™ | DE6P16OSPxxx | Twisted Pair | Yes | No | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 6 | Remee | PowerPipe™ | DE6P16OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 6 | Remee | PowerPipe™ | DE6P18OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 6 | Remee | PowerPipe™ | DE6P18OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 8 | Remee | PowerPipe™ | DE8P12OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/lan-premise-cables/activate-powered-cable-solutions/
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 12 | 8 | Remee | PowerPipe™ | DE8P12ISOSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/wp-content/uploads/2024/11/PowerPipe%E2%84%A2-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 8 | Remee | PowerPipe™ | DE8P14OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 8 | Remee | PowerPipe™ | DE8P14OSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/wp-content/uploads/2024/11/PowerPipe%E2%84%A2-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 8 | Remee | PowerPipe™ | DE8P16OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 16 | 8 | Remee | PowerPipe™ | DE8P16OSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/wp-content/uploads/2024/11/PowerPipe%E2%84%A2-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4, Wet Locations Direct Burial, Sun Resistant | 16 | 8 | EUPEN |  | HP16X16-CL4-B | Twisted Pair | No | No | Black
Direct Burial | CL4, Wet Locations Direct Burial, Sun Resistant | 16 | 8 | Proterial |  | WPN01613783 | Twisted Pair | No | No | Black
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 8 | Remee | PowerPipe™ | DE8P18OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 18 | 8 | Remee | PowerPipe™ | DE8P18OSPxxx | Twisted Pair | Yes | Yes | Green
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 12 | Remee | PowerPipe™ | DE8P14OSPxxx | Twisted Pair | Yes | No | Green | https://remee.com/wp-content/uploads/2024/08/PowerPipe™-OSP-DB-SR-No-Shield.pdf
Direct Burial | CL4Z, Direct Burial, Sun Resistant | 14 | 12 | Remee | PowerPipe™ | DE8P14OSPxxx | Twisted Pair | Yes | Yes | Green | https://remee.com/wp-content/uploads/2024/11/PowerPipe%E2%84%A2-OSP-DB-SR-No-Shield.pdf
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 1 | Marmon IEI | COM-Link® | C4C-P00U02-12-01 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 1 | Marmon IEI | COM-Link® | C4H-P00U02-12-01 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 1 | Marmon IEI | COM-Link® | C4C-P00U02-14-01 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 14 | 1 | Remee | PowerPipe™ | DE1P14RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 1 | Marmon IEI | COM-Link® | C4H-P00U02-14-01 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, LS-PVC, Sun Resistant | 14 | 1 | Proterial | Power+ | 42576-4 | Twisted Pair | Yes | No | Yellow
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 1 | Marmon IEI | COM-Link® | C4C-P00U02-16-01 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 16 | 1 | Remee | PowerPipe™ | DE1P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 1 | Marmon IEI | COM-Link® | C4H-P00U02-16-01 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, LS-PVC, Sun Resistant | 16 | 1 | Proterial | Power+ | 42564-4 | Twisted Pair | Yes | No | Yellow
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 1 | Marmon IEI | COM-Link® | C4C-P00U02-18-01 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 18 | 1 | Remee | PowerPipe™ | DE1P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 1 | Marmon IEI | COM-Link® | C4H-P00U02-18-01 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 2 | Marmon IEI | COM-Link® | C4C-P00U02-12-02 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 2 | Marmon IEI | COM-Link® | C4H-P00U02-12-02 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 2 | Marmon IEI | COM-Link® | C4C-P00U02-14-02 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 14 | 2 | Remee | PowerPipe™ | DE2P14RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 14 | 2 | Belden | FMPS Cables | DEIP142F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP142F
Plenum | CL4P, CMP, LS-PVC | 14 | 2 | Belden | FMPS Cables | DEIP142U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP142U
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 2 | Marmon IEI | COM-Link® | C4H-P00U02-14-02 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, LS-PVC, Sun Resistant | 14 | 2 | Proterial | Power+ | 42581-8 | Twisted Pair | Yes | No | Yellow
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 2 | Marmon IEI | COM-Link® | C4C-P00U02-16-02 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 16 | 2 | Remee | PowerPipe™ | DE2P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 16 | 2 | Belden | FMPS Cables | DEIP162F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP162F
Plenum | CL4P, CMP, LS-PVC | 16 | 2 | Belden | FMPS Cables | DEIP162U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP162U
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 2 | Marmon IEI | COM-Link® | C4H-P00U02-16-02 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, LS-PVC, Sun Resistant | 16 | 2 | Proterial | Power+ | 42577-8 | Twisted Pair | Yes | No | Yellow
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 2 | Marmon IEI | COM-Link® | C4C-P00U02-18-02 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 18 | 2 | Remee | PowerPipe™ | DE2P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 18 | 2 | Belden | FMPS Cables | DEIP182F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP182F
Plenum | CL4P, CMP, LS-PVC | 18 | 2 | Belden | FMPS Cables | DEIP182U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP182U
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 2 | Marmon IEI | COM-Link® | C4H-P00U02-18-02 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 3 | Marmon IEI | COM-Link® | C4C-P00U02-12-03 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 3 | Marmon IEI | COM-Link® | C4H-P00U02-12-03 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 3 | Marmon IEI | COM-Link® | C4C-P00U02-14-03 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 14 | 3 | Remee | PowerPipe™ | DE3P14RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 3 | Marmon IEI | COM-Link® | C4H-P00U02-14-03 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, LS-PVC, Sun Resistant | 14 | 3 | Proterial | Power+ | 42583-12 | Twisted Pair | Yes | No | Yellow
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 3 | Marmon IEI | COM-Link® | C4C-P00U02-16-03 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 16 | 3 | Remee | PowerPipe™ | DE3P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 3 | Marmon IEI | COM-Link® | C4H-P00U02-16-03 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, LS-PVC, Sun Resistant | 16 | 3 | Proterial | Power+ | 42563-12 | Twisted Pair | Yes | No | Yellow
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 3 | Marmon IEI | COM-Link® | C4C-P00U02-18-03 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 18 | 3 | Remee | PowerPipe™ | DE3P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 3 | Marmon IEI | COM-Link® | C4H-P00U02-18-03 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 4 | Marmon IEI | COM-Link® | C4C-P00U02-12-04 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 4 | Marmon IEI | COM-Link® | C4H-P00U02-12-04 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 4 | Marmon IEI | COM-Link® | C4C-P00U02-14-04 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 14 | 4 | Remee | PowerPipe™ | DE4P14RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 14 | 4 | Belden | FMPS Cables | DEIP144F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP144F
Plenum | CL4P, CMP, LS-PVC | 14 | 4 | Belden | FMPS Cables | DEIP144U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP144U
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 4 | Marmon IEI | COM-Link® | C4H-P00U02-14-04 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 4 | Marmon IEI | COM-Link® | C4C-P00U02-16-04 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 16 | 4 | Remee | PowerPipe™ | DE4P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 16 | 4 | Belden | FMPS Cables | DEIP164F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP164F
Plenum | CL4P, CMP, LS-PVC | 16 | 4 | Belden | FMPS Cables | DEIP164U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP164U
Plenum | CL4P, CMP | 16 | 4 | CommScope | Constellation® | P-016-HY-8G-F30YL/4X16AWG/CTX | Twisted Pair | Yes | No | Yellow | https://www.commscope.com/product-type/cables/hybrid-cables/item760255005/
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 4 | Marmon IEI | COM-Link® | C4H-P00U02-16-04 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, LS-PVC, Sun Resistant | 16 | 4 | Proterial | Power+ | 42587-28 | Twisted Pair | Yes | No | Yellow
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 4 | Marmon IEI | COM-Link® | C4C-P00U02-18-04 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 18 | 4 | Remee | PowerPipe™ | DE4P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 18 | 4 | Belden | FMPS Cables | DEIP184F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP184F
Plenum | CL4P, CMP, LS-PVC | 18 | 4 | Belden | FMPS Cables | DEIP184U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP184U
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 4 | Marmon IEI | COM-Link® | C4H-P00U02-18-04 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 6 | Marmon IEI | COM-Link® | C4C-P00U02-12-06 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 6 | Marmon IEI | COM-Link® | C4H-P00U02-12-06 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 6 | Marmon IEI | COM-Link® | C4C-P00U02-14-06 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 14 | 6 | Remee | PowerPipe™ | DE6P14RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 6 | Marmon IEI | COM-Link® | C4H-P00U02-14-06 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 6 | Marmon IEI | COM-Link® | C4C-P00U02-16-06 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 16 | 6 | Remee | PowerPipe™ | DE6P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P | 16 | 6 | Corning | ActiFi® | xxxZT8-61N01N20 | Linear Lay | Yes | No | Yellow | https://www.corning.com/catalog/coc/documents/product-family-specifications/0890_NAFTA_AEN.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 6 | Marmon IEI | COM-Link® | C4H-P00U02-16-06 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 6 | Marmon IEI | COM-Link® | C4C-P00U02-18-06 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 18 | 6 | Remee | PowerPipe™ | DE6P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 6 | Marmon IEI | COM-Link® | C4H-P00U02-18-06 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 8 | Marmon IEI | COM-Link® | C4C-P00U02-12-08 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 8 | Marmon IEI | COM-Link® | C4H-P00U02-12-08 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 8 | Marmon IEI | COM-Link® | C4C-P00U02-14-08 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 14 | 8 | Remee | PowerPipe™ | DE8P14RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 14 | 8 | Belden | FMPS Cables | DEIP148F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP148F
Plenum | CL4P, CMP, LS-PVC | 14 | 8 | Belden | FMPS Cables | DEIP148U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP148U
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 8 | Marmon IEI | COM-Link® | C4H-P00U02-14-08 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 8 | Marmon IEI | COM-Link® | C4C-P00U02-16-08 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 16 | 8 | Remee | PowerPipe™ | DE8P16RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 16 | 8 | Belden | FMPS Cables | DEIP168F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP168F
Plenum | CL4P, CMP, LS-PVC | 16 | 8 | Belden | FMPS Cables | DEIP168U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP168U
Plenum | CL4P | 16 | 8 | Corning | ActiFi® | xxxZT8-M1N01N20 | Linear Lay | Yes | No | Yellow | https://www.corning.com/catalog/coc/documents/product-family-specifications/0890_NAFTA_AEN.pdf
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 8 | Marmon IEI | COM-Link® | C4H-P00U02-16-08 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 8 | Marmon IEI | COM-Link® | C4C-P00U02-18-08 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P, CMP | 18 | 8 | Remee | PowerPipe™ | DE8P18RRxxx | Twisted Pair | Yes | No | Natural/Green | https://remee.com/wp-content/uploads/2024/11/REMEE-PowerPipe%E2%84%A2-CL4P-18-16-14-AWG.pdf
Plenum | CL4P, CMP, LS-PVC | 18 | 8 | Belden | FMPS Cables | DEIP188F | Twisted Pair | Yes | Yes | Green | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEIP188F
Plenum | CL4P, CMP, LS-PVC | 18 | 8 | Belden | FMPS Cables | DEIP188U | Twisted Pair | Yes | No | Green | https://www.belden.com/products/cable/power-cable/low-voltage-power-cable/digital-electricity-cable/deip188u
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 8 | Marmon IEI | COM-Link® | C4H-P00U02-18-08 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 12 | Marmon IEI | COM-Link® | C4C-P00U02-12-12 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 12 | Marmon IEI | COM-Link® | C4H-P00U02-12-12 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 12 | Marmon IEI | COM-Link® | C4C-P00U02-14-12 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 12 | Marmon IEI | COM-Link® | C4H-P00U02-14-12 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 12 | Marmon IEI | COM-Link® | C4C-P00U02-16-12 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 12 | Marmon IEI | COM-Link® | C4H-P00U02-16-12 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 12 | Marmon IEI | COM-Link® | C4C-P00U02-18-12 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 12 | Marmon IEI | COM-Link® | C4H-P00U02-18-12 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 12 | 16 | Marmon IEI | COM-Link® | C4C-P00U02-12-16 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 12 | 16 | Marmon IEI | COM-Link® | C4H-P00U02-12-16 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 14 | 16 | Marmon IEI | COM-Link® | C4C-P00U02-14-16 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 14 | 16 | Marmon IEI | COM-Link® | C4H-P00U02-14-16 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 16 | 16 | Marmon IEI | COM-Link® | C4C-P00U02-16-16 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 16 | 16 | Marmon IEI | COM-Link® | C4H-P00U02-16-16 | Twisted Pair | Yes | Optional | White/Custom
Plenum | CL4P, CL3P, CMP, LS-PVC | 18 | 16 | Marmon IEI | COM-Link® | C4C-P00U02-18-16 | Twisted Pair | No | Optional | White/Custom | https://marmon.concoraspec.com/products/43410b0d-1bc6-4178-a69b-74fd9a5593ba
Plenum | CL4P-OF, CL3P-OF, CMP-OF, LS-PVC | 18 | 16 | Marmon IEI | COM-Link® | C4H-P00U02-18-16 | Twisted Pair | Yes | Optional | White/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-12-01SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-12-01SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-14-01SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-14-01SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-16-01SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-16-01SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-18-01SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-18-01SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-12-02SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-12-02SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-14-02SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 14 | 2 | Belden | FMPS Cables | DEDN142U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN142F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 14 | 2 | Belden | FMPS Cables | DEDN142F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN142F
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-14-02SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-16-02SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-16-02SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162F
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 16 | 2 | Southwire | CL4SS® | CL4Z162N0605x | Twisted Pair | No | No | Green/Black/White
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 16 | 2 | Southwire | CL4SS® | CL4Z162S0608 | Twisted Pair | No | Yes | Green/Black/White
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-18-02SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182F
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 18 | 2 | Southwire | CL4SS® | CL4Z182N0605x | Twisted Pair | No | No | Green/Black/White
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 18 | 2 | Southwire | CL4SS® | CL4Z182S0608 | Twisted Pair | No | Yes | Green/Black/White
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-18-02SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-12-03SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-12-03SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-14-03SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-14-03SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-16-03SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-16-03SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-18-03SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-18-03SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-12-04SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-12-04SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-14-04SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 14 | 4 | Belden | FMPS Cables | DEDN144U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN144F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 14 | 4 | Belden | FMPS Cables | DEDN144F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN144F
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-14-04SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-16-04SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-16-04SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164F
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 16 | 4 | Southwire | CL4SS® | CL4Z164N0605x | Twisted Pair | No | No | Green/Black/White
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 16 | 4 | Southwire | CL4SS® | CL4Z164S0608 | Twisted Pair | No | Yes | Green/Black/White
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-18-04SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184F
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 18 | 4 | Southwire | CL4SS® | CL4Z184N0605x | Twisted Pair | No | No | Green/Black/White
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 18 | 4 | Southwire | CL4SS® | CL4Z184S0608 | Twisted Pair | No | Yes | Green/Black/White
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-18-04SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-12-06SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-12-06SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-14-06SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-14-06SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-16-06SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-16-06SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R | 16 | 6 | Corning | ActiFi® | xxxZTF-61N01N20 | Linear Lay | Yes | No | Yellow | https://www.corning.com/catalog/coc/documents/product-family-specifications/0890_NAFTA_AEN.pdf
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-18-06SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-18-06SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-12-08SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-12-08SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-14-08SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 14 | 8 | Belden | FMPS Cables | DEDN148U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN148F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 14 | 8 | Belden | FMPS Cables | DEDN148F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN148F
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-14-08SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-16-08SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-16-08SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168F
Riser | CL4R | 16 | 8 | Corning | ActiFi® | xxxZTF-M1N01N20 | Linear Lay | Yes | No | Yellow | https://www.corning.com/catalog/coc/documents/product-family-specifications/0890_NAFTA_AEN.pdf
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 16 | 8 | Southwire | CL4SS® | CL4Z168N0605x | Twisted Pair | No | No | Green/Black/White
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 16 | 8 | Southwire | CL4SS® | CL4Z168S0608 | Twisted Pair | No | Yes | Green/Black/White
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 18 | 8 | Southwire | CL4SS® | CL4Z188S0608 | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-18-08SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188U | Twisted Pair | Optional | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188F
Riser | CL4Z, CMG, Wet Locations, Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188F
Riser | CL4Z, CMG, FT4 LS-PVC, Wet Locations | 18 | 8 | Southwire | CL4SS® | CL4Z188N0605x | Twisted Pair | No | No | Green/Black/White
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-18-08SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-12-12SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-12-12SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-14-12SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-14-12SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-16-12SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-16-12SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-18-12SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-18-12SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-12-16SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-12-16SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-14-16SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-14-16SW | Twisted Pair | Yes | Optional | *Black/Custom
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-16-16SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-16-16SW | Twisted Pair | Yes | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-18-16SW | Twisted Pair | No | Optional | *Black/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Riser | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-18-16SW | Twisted Pair | Yes | Optional | *Black/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-12-01SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-12-01SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 12 | 1 | Marmon IEI | COM-Link® | C4C-G00U01-12-01SW | Twisted Pair | No | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-14-01SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 14 | 1 | Marmon IEI | COM-Link® | C4C-G00U01-14-01SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-14-01SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-16-01SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-16-01SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 16 | 1 | Marmon IEI | COM-Link® | C4C-G00U01-16-01SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 1 | Marmon IEI | COM-Link® | C4C-R00U01-18-01SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 1 | Marmon IEI | COM-Link® | C4H-R00U01-18-01SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 18 | 1 | Marmon IEI | COM-Link® | C4C-G00U01-18-01SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-12-02SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 12 | 2 | Marmon IEI | COM-Link® | C4C-G00U01-12-02SW | Twisted Pair | No | Optional | Black*/Custom
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-12-02SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 14 | 2 | Southwire | CL4SS® | CL4Z142S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-14-02SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 14 | 2 | Marmon IEI | COM-Link® | C4C-G00U01-14-02SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CMG, Wet Locations, Sun Resistant | 14 | 2 | Belden | FMPS Cables | DEDN142U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN142F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 14 | 2 | Belden | FMPS Cables | DEDN142F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN142F
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 14 | 2 | Southwire | CL4SS® | CL4Z142N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-14-02SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 16 | 2 | Southwire | CL4SS® | CL4Z162S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-16-02SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-16-02SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 16 | 2 | Marmon IEI | COM-Link® | C4C-G00U01-16-02SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CMG, Wet Locations, Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 16 | 2 | Belden | FMPS Cables | DEDN162F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN162F
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 16 | 2 | Southwire | CL4SS® | CL4Z162N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 18 | 2 | Southwire | CL4SS® | CL4Z182S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 2 | Marmon IEI | COM-Link® | C4C-R00U01-18-02SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 2 | Marmon IEI | COM-Link® | C4H-R00U01-18-02SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 18 | 2 | Marmon IEI | COM-Link® | C4C-G00U01-18-02SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 18 | 2 | Southwire | CL4SS® | CL4Z182N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4, CMG, Wet Locations, Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 18 | 2 | Belden | FMPS Cables | DEDN182F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN182F
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-12-03SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-12-03SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 12 | 3 | Marmon IEI | COM-Link® | C4C-G00U01-12-03SW | Twisted Pair | No | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-14-03SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 14 | 3 | Marmon IEI | COM-Link® | C4C-G00U01-14-03SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-14-03SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-16-03SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-16-03SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 16 | 3 | Marmon IEI | COM-Link® | C4C-G00U01-16-03SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 3 | Marmon IEI | COM-Link® | C4C-R00U01-18-03SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 3 | Marmon IEI | COM-Link® | C4H-R00U01-18-03SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 18 | 3 | Marmon IEI | COM-Link® | C4C-G00U01-18-03SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-12-04SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-12-04SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 12 | 4 | Marmon IEI | COM-Link® | C4C-G00U01-12-04SW | Twisted Pair | No | Optional | Black*/Custom
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 14 | 4 | Southwire | CL4SS® | CL4Z144S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-14-04SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 14 | 4 | Marmon IEI | COM-Link® | C4C-G00U01-14-04SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CMG, Wet Locations, Sun Resistant | 14 | 4 | Belden | FMPS Cables | DEDN144U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN144F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 14 | 4 | Belden | FMPS Cables | DEDN144F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN144F
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 14 | 4 | Southwire | CL4SS® | CL4Z144N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-14-04SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 16 | 4 | Southwire | CL4SS® | CL4Z164S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-16-04SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-16-04SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 16 | 4 | Marmon IEI | COM-Link® | C4C-G00U01-16-04SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CMG, Wet Locations, Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 16 | 4 | Belden | FMPS Cables | DEDN164F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN164F
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 16 | 4 | Southwire | CL4SS® | CL4Z164N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 18 | 4 | Southwire | CL4SS® | CL4Z184S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 4 | Marmon IEI | COM-Link® | C4C-R00U01-18-04SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 4 | Marmon IEI | COM-Link® | C4H-R00U01-18-04SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 18 | 4 | Marmon IEI | COM-Link® | C4C-G00U01-18-04SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 18 | 4 | Southwire | CL4SS® | CL4Z184N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4, CMG, Wet Locations, Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 18 | 4 | Belden | FMPS Cables | DEDN184F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN184F
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-12-06SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-12-06SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 12 | 6 | Marmon IEI | COM-Link® | C4C-G00U01-12-06SW | Twisted Pair | No | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-14-06SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 14 | 6 | Marmon IEI | COM-Link® | C4C-G00U01-14-06SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-14-06SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-16-06SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-16-06SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 16 | 6 | Marmon IEI | COM-Link® | C4C-G00U01-16-06SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 6 | Marmon IEI | COM-Link® | C4C-R00U01-18-06SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 6 | Marmon IEI | COM-Link® | C4H-R00U01-18-06SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 18 | 6 | Marmon IEI | COM-Link® | C4C-G00U01-18-06SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-12-08SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-12-08SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 12 | 8 | Marmon IEI | COM-Link® | C4C-G00U01-12-08SW | Twisted Pair | No | Optional | Black*/Custom
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 14 | 8 | Southwire | CL4SS® | CL4Z148S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-14-08SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 14 | 8 | Marmon IEI | COM-Link® | C4C-G00U01-14-08SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CMG, Wet Locations, Sun Resistant | 14 | 8 | Belden | FMPS Cables | DEDN148U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN148F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 14 | 8 | Belden | FMPS Cables | DEDN148F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN148F
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 14 | 8 | Southwire | CL4SS® | CL4Z148N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-14-08SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 16 | 8 | Southwire | CL4SS® | CL4Z168S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-16-08SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-16-08SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 16 | 8 | Marmon IEI | COM-Link® | C4C-G00U01-16-08SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CMG, Wet Locations, Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 16 | 8 | Belden | FMPS Cables | DEDN168F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN168F
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 16 | 8 | Southwire | CL4SS® | CL4Z168N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 18 | 8 | Southwire | CL4SS® | CL4Z188S060x | Twisted Pair | No | Yes | Green/Black/White | https://cabletechsupport.southwire.com/en/tile/39/spec/13008/?country=US
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 8 | Marmon IEI | COM-Link® | C4C-R00U01-18-08SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 8 | Marmon IEI | COM-Link® | C4H-R00U01-18-08SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4, CL3 CMG FT4, AWM 2464, Wet Locations, Sun Resistant* | 18 | 8 | Marmon IEI | COM-Link® | C4C-G00U01-18-08SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4Z, CMG, LS-PVC, Wet Locations | 18 | 8 | Southwire | CL4SS® | CL4Z188N060x | Twisted Pair | No | No | Green/Black/White | https://www.belden.com/products/cable/power-cable/digital-electricity-cable/dedn168u
Wet | CL4, CMG, Wet Locations, Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188U | Twisted Pair | Yes | No | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188F
Wet | CL4, CMG, Wet Locations, Sun Resistant | 18 | 8 | Belden | FMPS Cables | DEDN188F | Twisted Pair | Yes | Yes | Black | https://www.belden.com/products/Cable/Power-Cable/Digital-Electricity-Cable/DEDN188F
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-12-12SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-12-12SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-14-12SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-14-12SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-16-12SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-16-12SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 12 | Marmon IEI | COM-Link® | C4C-R00U01-18-12SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 12 | Marmon IEI | COM-Link® | C4H-R00U01-18-12SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 12 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-12-16SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 12 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-12-16SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 14 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-14-16SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 14 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-14-16SW | Twisted Pair | Yes | Optional | Black*/Custom
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 16 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-16-16SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 16 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-16-16SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R, CL3R, Wet Locations, Sun Resistant* | 18 | 16 | Marmon IEI | COM-Link® | C4C-R00U01-18-16SW | Twisted Pair | No | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f
Wet | CL4R-OF, CL3R-OF, Wet Locations, Sun Resistant* | 18 | 16 | Marmon IEI | COM-Link® | C4H-R00U01-18-16SW | Twisted Pair | Yes | Optional | Black*/Custom | https://marmon.concoraspec.com/products/e8e591f3-2a62-4058-b0f4-94ea218b893f

## Environment Guide
Environment Guide
Determine the Class 4 installation environment before selecting cable
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Environment | Common location | Required rating family | Selection rule | Do not assume
Plenum | Air-return ceilings and environmental air spaces | CL4P | May also be used in risers | Cable must be UL 1400-2 certified with CL4 marking.
Riser | Vertical shafts and between-floor pathways | CL4R | Use only where plenum rating is not required | Not permitted in plenum spaces unless CL4P rated.
Wet | Outdoor ducts, wet pathways, and general-purpose indoor/outdoor routes | CL4 or CL4Z plus applicable listings | Confirm wet-location and sunlight-resistance markings | Not direct burial unless specifically listed.
Direct Burial | Below-grade installation without added raceway protection | CL4 or CL4Z with Direct Burial marking | Confirm sunlight resistance and building-entry transition | Direct-burial rating does not replace required interior fire rating.

## Ratings Guide
Cable Rating Guide
Use project specifications and applicable code to confirm the required Class 4 listing.
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Marking | Meaning | Typical application | Engineering note
CL4 | General-purpose Class 4 cable, 450 V | General-purpose, outdoor, or direct burial only where specifically listed | Must be certified to UL 1400-2 with CL4 marking on the jacket.
CL4P | Class 4 plenum cable | Plenum and riser | Required for plenum deployments; may be used in risers.
CL4R | Class 4 riser cable | Riser and qualifying in-wall pathways | Not permitted in plenum spaces.
CL4Z | Outdoor-only Class 4 designation | Outdoor use | Not to be attached to or used within a building structure unless otherwise designated.
WET | Continuous wet location | Conduit or ducts | In addition to CL4 rating. Confirm CL4 marking and building-entry transition requirements. Does not automatically mean direct burial.
DB / DIR BUR | Direct burial | Below grade without added protection | In addition to CL4 rating. Confirm CL4 marking and building-entry transition requirements.

## Color Codes
Manufacturer Wire Color Codes
Use the information below for conductor maps.
support@voltserver.com ¦ 888-622-8658, Option 1 ¦ www.VoltServer.com
Pair # | Belden | CommScope | EUPEN | MarmonIEI | Proterial | Remee | Southwire | Corning
1 | Black/Red | Red/White | Black/Red | Black/Red | Black/Red | Black/Red | Black/Red | Telcordia
2 | Black/White | Black/White | Black/White | Black/White | Black/White | Black/White | Black/White
3 | Black/Green | Blue/White | Black/Green | Black/Green | Black/Green | Black/Green | Black/Green
4 | Black/Blue | Brown/White | Black/Blue | Black/Blue | Black/Blue | Black/Blue | Black/Blue
5 | Black/Yellow |  | Black/Yellow | Black/Yellow | Black/Yellow | Black/Yellow | Black/Yellow
6 | Black/Brown |  | Black/Brown | Black/Brown | Black/Brown | Black/Brown | Black/Brown
7 | Black/Orange |  | Black/Orange | Black/Orange | Black/Orange | Black/Orange | Black/Orange
8 | Red/White |  | Red/White | Red/White | Red/White | Red/White | Black/White
9 |  |  |  | Red/Green
10 |  |  |  | Red/Blue
11 |  |  |  | Red/Yellow
12 |  |  |  | Red/Brown
13 |  |  |  | Red/Orange
14 |  |  |  | White/Green
15 |  |  |  | White/Blue
16 |  |  |  | White/Yellow

## MFR Directory
Manufacturer & Procurement Directory
Confirm current Class 4 cable specifications, availability, and ordering details with the manufacturer or distributor
Manufacturer | How to buy/contact | Product information
Belden | Belden - Find-A-Distributor | Belden FMPS Cables
CommScope | CommScope - How to Buy | CommScope - Constellation Plenum Hybrid Class 4 Cable
Corning | Corning Authorized Distributors | Corning - Actifi
EUPEN | EUPEN - Contact Us
MarmonIEI | Marmon IEI - Contact Us | Marmon IEI - Class 4 Cables
Proterial | Proterial - Sales Offices | Proterial - Cable Systems
Remee | Remee - Request for Information | Remee - Activate Powered Cable Solutions
Southwire | Southwire - Where-to-Buy | Southwire CL4SS™ Class 4 Non-Shielded Gen. Purpose Outdoor
Southwire CL4SS™ Class 4 Shielded Outdoor / General Purpose